Emergency Power Control for Dimmable Emergency Fixtures (EPC-D-F-ATS)  Specification

1      Electrical Specifications

  - The EPC-D-F-ATS shall automatically illuminate connected emergency loads to full brightness upon utility power interruption, regardless of switch/dimmer position. (NEC 700.24)

  - The EPC-D-F-ATS shall be compatible with 2-wire, 3-wire, 0-10V, & DALI/EcoSystem dimming systems & ballasts.

  - The same local room switch, dimmer, or lighting control shall dim both regular & emergency luminaires at the same level during normal operation.

  - The EPC-D-F-ATS shall have a minimum load rating of 16 Amps at 120V or 277V , and be rated for Tungsten and Ballast loads.

  - The EPC-D-F-ATS shall accept (120-277V) 50-60Hz Input & Output (voltage tolerance +/- 15%).

  - The EPC-D-F-ATS shall include emergency power & regular power indicator LED’s & a manual test switch which are visible to room occupants when installed flush. (UL924 Section 29)

  - The EPC-D-F-ATS shall accept separate phases on the regular hot , emergency hot, and dimmed hot inputs.

  - The EPC-D-F-ATS shall include high voltage input surge protection up to 50,000V.

1.10 Load contacts shall be able to withstand 10 direct shorts while connected to 20 Amp breaker without permanent damage.

1.11 The EPC-D-F-ATS shall not generate any objectionable electrical or mechanical noise.

- Mechanical Specifications

  - The EPC-D-F-ATS shall mount inside a 4-11/16” junction box with an extension box. (total depth at least 4”).

  - The EPC-D-F-ATS shall be installed flush to the ceiling so that test switch & LED’s are in plain view of room occupants as required by some local electrical codes.

  - The EPC-D-F-ATS shall have UL94-V0 or UL94-5VA flame rating.

  - Enclosure shall be white

  - Dimensions:  flush mounted size: 6” x 6” x 1/2”  body size: 4” x 4” x 2.3”

- General Specifications

3.1  The EPC-D-F shall be UL1008 listed.

3.2  Warranty shall be 5 year replacement warranty

3.3  The EPC shall comply with all applicable N.E.C., N.F.P.A, OSHA, & local safety codes.

Emergency Power Control shall be model EPC-D-F-ATS

by LVS, Inc. 800-982-4587  www.lvscontrols.com